FOX MODEL FT2A FLOW METER PROCUREMENT SPECIFICATION

- The flow meter shall operate on the Constant Delta Temperature (Constant Δ T) thermal mass principal. The sensing elements shall consist of two platinum RTD's. The sensor's heated element shall operate a constant temperature of approximately 40°F above the gas temperature.

- The flow meter shall have a built-in display of flow rate, flow total, temperature, and elapsed time. The read-out shall utilize a backlit LCD display consisting of two lines each 16 characters.

- Two 4-20mA outputs are required; one output for flow rate and the second output is programmable for flow rate or process temperature. A pulse output is also required.

- An optional non-resetting totalizer shall be available as required by air quality management districts.

- A 4-key keypad will be employed for user programming. Input parameters shall be protected by use of a password. Nonvolatile memory will retain the last totalizer value and user parameters for up to seven (7) years.

- The flow meter shall have a built-in microprocessor allowing field programmability of the 4mA setting, 20mA setting, pulse output setting, pipe/duct area, zero flow cutoff and alarm settings.

- The flow meter will be FM (U.S.) & FMc (CANADA) approved for Class I, II, III, Division 2, Groups A, B, C, D, E, F, G, T4A hazardous locations. NEMA 4X and CE approved.

- The flow meter shall measure gas flows over a range of 0-60,000 standard feet per minute. Sensor response time shall be 0.9 seconds for a one (1) Sigma change in velocity.

- Accuracy shall be ±1.0 percent of reading, ±0.2 percent of full scale and repeatability ±0.2 percent of full scale over an operating temperature range of -40°F to 250°F.

- All wetted parts are to be 316SS utilizing an all welded design. Other alloys will optionally be available.

- All electronics to be mounted in a single NEMA 4X enclosure. Input power will be 24VDC or 100-240VAC, 50-60 Hz.

- USB serial communication port is standard; the following communication options are also available: RS485 Modbus, BACnet MS/TP, Profibus-DP, DeviceNet, or Ethernet Modbus TCP.

- The manufacturer shall provide an NIST-traceable calibration certificate for the instrument.

- The flow meter will have internal self-diagnostics without requiring external equipment to evaluate meter performance.

- The instrument will be the Model FT2A manufactured by Fox Thermal, 399 Reservation Road, Marina, CA 93933 Phone: 831-384-4300, Fax: 831-384-4312, Email: sales@foxthermal.com, Website: www.foxthermal.com