FOX MODEL FT4X FLOW METER PROCUREMENT SPECIFICATION

- The flow meter shall operate on the Constant Delta Temperature (Constant Δ T) thermal mass principal.

- A DDC-Sensor™ (Direct Digitally Controlled sensor) shall be standard.

- The Gas-SelectX® menu will offer pre-programmed and selectable gases and gas mixtures.

- The flow meter will have CAL-V™ calibration validation feature that verifies the meter is operating accurately.

- The flow meter will have a standard Data Logger for 40 24-hour daily totals; 7+ year history of alarm/event logs.

- The flow meter shall have a built-in display of flow rate, flow total, temperature, and elapsed time. The read-out shall utilize a backlit LCD display consisting of two lines each 16 characters.

- A 4-key keypad will be employed for user programming. Input parameters shall be protected by use of a password. Nonvolatile memory will retain totalizer and user parameters for up to seven (7) years.

- Two 4-20mA outputs are required; one output for flow rate and a HART communication option; a second output is programmable for flow rate or process temperature. A pulse output is also required.

- The flow meter shall have a built-in microprocessor allowing field programmability of the 4mA setting, 20mA setting, pulse output setting, pipe diameter, zero flow cutoff, standard temperature and pressure (STP), and alarm settings.

- The flow meter shall be compliant with agency approvals from CE, FM/FMc, ATEX, IECEx, and UKEX for use in potentially explosive atmospheres.

- The flow meter shall measure gas flows over a range of 15-60,000 standard feet per minute. Sensor response time shall be 0.8 seconds (one time constant).

- Operating temperature range -40°F to 250°F. Flow measurement accuracy: ±1.0 percent of reading, ±0.2 percent of full scale. Other gases: ±1.5 percent of reading, ±0.5 percent of full scale. Repeatability: ±0.2 percent of full scale.

- All wetted parts are to be 316 stainless steel all welded design. Other alloys will optionally be available for inline flow bodies.

- All electronics to be mounted in a single NEMA 4X enclosure. Input power will be 12-28VDC or 100-240VAC, 50-60 Hz.

- The flow meter shall be made available in insertion, inline, and remote styles.

- USB serial communication port is standard; the following communication options are also available: RS485 Modbus RTU and HART.

- The manufacturer shall provide an NIST-traceable calibration certificate for the instrument.

- The instrument will be the Model FT4X manufactured by Fox Thermal, 399 Reservation Road, Marina, CA 93933 Phone: 831-384-4300, Email: sales@foxthermal.com, Website: www.foxthermal.com